# Default Parameters, Required Inputs and Assessment Methodology

In the following default parameters, required user inputs and the assessment methodology to be used for the 5GDHC Quick Check Tool is described. They are intended for a preliminary screening rather than a detailed system design. The parameters, inputs and methodology are based on simplified assumptions and should be interpreted carefully. Actual values may vary depending on project-specific conditions and should be refined through further analysis.

## Default Parameters and Assumptions

To enable a quick and consistent assessment, the tool uses predefined default values for building energy demand, average floor area, and the potential energy supply from different sources. These values allow users to perform an initial assessment without having to provide detailed building-level data.

Buildings are grouped into the following categories according to their use:

- Residential buildings: Residential buildings of different construction periods.

- Category A: Retail, museums, supermarkets, schools, offices and fitness studios.

- Category B: Kindergartens, sports halls, hotels and theatres.

- Category C: Hospitals, restaurants, swimming pools and canteens.

- Industry: Industrial buildings and facilities.

Each building category is associated with default values for annual heating demand, annual cooling demand and average. floor area. The applicable values depend on the building's construction period.

## Default Building Parameters

The following tables provide the predefined values to be used by the Quick Check Tool:

Table 1: Annual Heating Demand: Default annual heating demand per square meter of floor area expressed in kWh/m² per year

|  |  | Construction Period |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | -1919 | 1919-1960 | 1961-1990 | 1991-2010 | 2011-today |
| Type | Residential buildings | 124.4 | 131.5 | 109.3 | 92.5 | 86.3 |
|  | Category A | 139.0 | 127.4 | 104.3 | 92.7 | 67.5 |
|  | Category B | 177.0 | 162.3 | 132.8 | 118.0 | 78.8 |
|  | Category C | 204.0 | 187.0 | 153.0 | 136.0 | 90.0 |
|  | Industry* | - | - | - | - | - |

Table 2: Annual Cooling Demand: Default annual cooling demand per square meter of floor area expressed in kWh/m² per year

|  |  | Construction Period |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | -1919 | 1919-1960 | 1961-1990 | 1991-2010 | 2011-today |
| Type | Residential buildings | 10.0 | 14.0 | 11.0 | 8.5 | 5.0 |
|  | Category A | 5.4 | 7.8 | 6.0 | 4.8 | 4.2 |
|  | Category B | 6.8 | 9.8 | 7.5 | 6.0 | 5.3 |
|  | Category C | 5.2 | 7.5 | 5.8 | 4.6 | 4.0 |
|  | Industry* | - | - | - | - | - |

Table 3: Average Floor Area: Default average floor area per building expressed in m².

|  |  | Construction Period |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | -1919 | 1919-1960 | 1961-1990 | 1991-2010 | 2011-today |
| Type | Residential buildings | 547.5 | 452.5 | 493.0 | 408.0 | 347.8 |
|  | Category A | 933.3 | 991.7 | 1050.0 | 1108.0 | 1166.7 |
|  | Category B | 1420.0 | 1508.8 | 1597.5 | 1686.3 | 1775.0 |
|  | Category C | 730.0 | 775.6 | 821.3 | 866.9 | 912.5 |
|  | Industry* | - | - | - | - | - |

The provided tables do not include default values for industrial buildings. If industry is included in the project area, the overall assessment shall automatically be set to “Further analysis required”.

## Default Energy Source Parameters

The following tables provide predefined annual energy supply potentials for different energy sources at three levels: low, medium and high. They also specify the corresponding coefficients of performance (COP) where applicable. The available energy sources are described below. The capacities shown in the following tables are the energy extracted from the source and NOT the thermal energy delivered to the building. Therefore, the COP has to be considered, as shown in Section 3.

Table 4: Heating Capacity per Source in kWh/a

| Source | Low | Medium | High | COP |
| --- | --- | --- | --- | --- |
| Geothermal | 10,000 | 50,000 | 150,000 | 4.5 |
| Waste heat | 5,000 | 30,000 | 100,000 | 4.5 |
| Ground water | 10,000 | 50,000 | 150,000 | 5.0 |
| Surface water | 10,000 | 50,000 | 150,000 | 4.0 |
| Solar thermal | 5,000 | 20,000 | 50,000 | - |
| Ambient air | 10,000 | 50,000 | 150,000 | 3.0 |

Table 5: Cooling Capacity per Source in kWh/a

| Source | Low | Medium | High | COP |
| --- | --- | --- | --- | --- |
| Geothermal | 10,000 | 50,000 | 150,000 | 5.0 |
| Waste heat | - | - | - | - |
| Ground water | 10,000 | 50,000 | 150,000 | 5.0 |
| Surface water | 10,000 | 50,000 | 150,000 | 4.5 |
| Solar thermal | - | - | - | - |
| Ambient air | 10,000 | 50,000 | 150,000 | 3.5 |

Users select the energy sources available in the project area and indicate their estimated potential as low, medium, high or unknown. The tool should use the corresponding predefined values to estimate the annual heating and cooling supply potential. If the potential of a selected source is unknown, the overall assessment must automatically be set to “Further analysis required”. A dash in the tables indicates that no default capacity is provided for that source and application.

Photovoltaic (PV) systems can be considered as an additional feature. Its potential effect on electricity costs shall be incorporated with an applicable reduction factor of 30%.

## Economic Parameters

The following table shows the economic parameters required to estimate the economic viability of a potential 5GDHC network. The parameters listed are only preliminary assumptions. Therefore, the results must be treated carefully.

Table 4: Economic Parameters

| Parameter | Default Value | Unit |
| --- | --- | --- |
| Heating base price | 6.00 | €/m² |
| Heating energy price | 0.12 | €/kWh |
| Cooling base price | 3.00 | €/m² |
| Cooling energy price | 0.08 | €/kWh |
| Connection fee | 1000 | €/building |
| Network construction costs (pipes, materials, excavation and installation) | 500 | €/m |
| Geothermal installation costs | 1.50 | €/(kWh/a) |
| Waste heat installation costs | 0.50 | €/(kWh/a) |
| Ground water installation costs | 1.00 | €/(kWh/a) |
| Surface water installation costs | 0.80 | €/(kWh/a) |
| Solar thermal installation costs | 0.70 | €/(kWh/a) |
| Ambient air installation costs | - | €/kWh |
| Heat pump | 15,000 | €/building |
| Electricity cost | 0.20 | €/kWh |
| PV cost reduction | 30 | % |
| Depriciation period | 20 | a |
| Interest rate | 3 | % |

# Required Inputs

The Quick Check Tool should guide users through a structured input process. Below the inputs required are shortly described.

## Project Area

- Total number of buildings

- Total project area in m²

- Building density (rural, sub-urban, urban)

Exact building density is calculated automatically from the total number of buildings and the project area.

## Building Type and Construction Period

Users specify the relative share of each building type and construction period within the project area. The distribution can be entered in a table, with building types as rows and construction periods as columns. The sum of all shares must equal 100%. For example, a project area could consist of:

- 50% residential buildings constructed between 1991 and 2010

- 25% residential buildings constructed between 2011 and today

- 25% Category A buildings constructed between 2011 and today

The tool uses these shares to estimate the number of buildings in each category and calculate their corresponding heating and cooling demand. If the user has more detailed information about the buildings' energy demand, manual input of heating and cooling demand should be available as an optional alternative to the default estimates.

## Energy Sources and Supply Potential

Users select the energy sources available or potentially available in the project area. For each selected source, they indicate its potential as:

- Low

- Medium

- High

- Unknown

The tool assigns the corresponding predefined annual supply capacity and COP, where applicable. If any selected source has an unknown potential, the overall assessment must automatically be “Further analysis required”. The tool should explain that the source potential needs to be clarified before a reliable initial assessment can be made.

## Network Length

Users may optionally enter the estimated total network length. If no value is provided, the tool estimates the network length using the predefined calculation method described in Section 3. The tool should indicate whether the network length was entered manually or estimated.

# Calculation Methodology

The Quick Check Tool implements the predefined calculation methodology to estimate building energy demand, network length, energy supply coverage and the main indicators influencing the assessment. All calculations should be performed automatically once the user has entered the required project data.

## Number of Buildings per Type and Construction Period

Ni,p= Ntotal⋅ si,p

Ni,p … Number of buildings of type i and construction period p

Ntotal … Total number of buildings

si,p  … Share of building type i an construction period p in %

## Annual Heating and Cooling Demand

The annual heating demand for each building category is calculated using the estimated number of buildings, the default heating demand per square meter and the average floor area.

Qheat=Ni,p⋅qheat⋅A

Qheat … Annual heating demand for building type i and construction period p in kWh/a

Ni,p … Number of buildings of type i and construction period p

qheat … default heating demand per building type i and construction period p in kWh/m²

A … default floor area per building type i and construction period p in m²

Qcool=Ni,p⋅qcool⋅A

Qcool … Annual cooling demand for building type i and construction period p in kWh/a

Ni,p … Number of buildings of type i and construction period p

qcool … default cooling demand per building type i and construction period p in kWh/m²

A … default floor area per building type i and construction period p in m²

The total annual heating and cooling demand is obtained by summing the demand across all building types and construction periods. These totals represent the estimated annual energy demand of the entire project area.

Qheat, total= i=1np=1mQheat

Qheat, total … total annual heating demand of all buildings in kWh/a

n … number of building types

m … number of construction periods

Qcool, total= i=1np=1mQcool,i,p

Qcool, total … total annual heating demand of all buildings in kWh/a

n … number of building types

m … number of construction periods

## Building Density

Building density describes how many buildings are located within one hectare of the project area.

ρbuilding=Ntotal⋅104Aproj

ρbuilding … building density of project area in buildings/ha

Ntotal … Total number of buildings

Aproj … total project area in m²

## Estimated Network Length

If no network length is entered manually, the tool estimates the required network length using the following predefined relationship:

lspec=171.221+8.817⋅e-0.549 ⋅Nha

lspec … specific net length

Nha … number of buildings per hectare

ltotal=lspec⋅Aproj104

ltotal … total net length in m

lspec … specific net length in m/ha

Aproj … total project area in m²

## Heat Density

Heat density relates the total annual heating demand to the estimated network length. This indicator helps assess how much heating demand can be served relative to the length of network required. Higher heat density can improve the economic outlook because more heating demand is served per meter of network.

ρheat=Qheat,totalltotal

ρheat … heat density of project area in kWh/m

Qheat, total … total annual heating demand of all buildings in kWh/a

ltotal … total net length in m

## Heating and Cooling Supply Coverage

The tool compares the available energy supply with the corresponding annual demand. Coverage values indicate the proportion of the annual demand that can be supplied by the selected energy sources. A value of 1.0 corresponds to 100% coverage. The tool should display heating and cooling coverage separately to make potential supply gaps transparent.

Cheat=Qheat, supplyQheat, total

Cheat … heating demand coverage

Qheat,supply … annual heating supply per source in kWh/a

Qheat, total … total annual heating demand of all buildings in kWh/a

Ccool=Qcool, supplyQcool, total

Ccool … cooling demand coverage

Qcool,supply … annual cooling supply per source in kWh/a

Qcool, total … total annual cooling demand of all buildings in kWh/a

## Cooling-to-Heating Demand Ratio

The cooling-to-heating ratio indicates how balanced the annual heating and cooling demands are. A value of 1 indicates equal heating and cooling demands, while values approaching 0 indicate an increasing imbalance. This indicator should be interpreted together with the other technical and economic indicators. An unbalanced demand profile does not automatically make a 5GDHC network unsuitable.

## Heating and Cooling Supply

Qheat, supply=Qheat,available⋅COPCOP-1

Qheat,supply … annual heating supply per source in kWh/a

Qheat,available … total heating energy provided by sources in kWh/a

COP … Coefficient of power of heat pump per source

Qcool, supply=Qcool,available⋅COPCOP+1

Qcool,supply … annual cooling supply per source in kWh/a

Qcool,available … total cooling energy provided by sources in kWh/a

COP … Coefficient of power of heat pump per source

## Annual Heating and Cooling Revenues

Rheat=i=1np=1m(Ni,p⋅A⋅pH,base)+ Qheat, total⋅pH,energy

Rheat … Annual heating revenue in €/a

A … default floor area per building type i and construction period p in m²

pH,base … heating base price in €/m²

Qheat, total … total annual heating demand of all buildings in kWh/a

pH,energy … heating energy price in €/kWh

Rcool=i=1np=1m(Ni,p⋅A⋅pC,base)+ Qcool, total⋅pC,energy

Rcool … Annual cooling revenue in €/a

A … default floor area per building type i and construction period p in m²

pC,base … cooling base price in €/m²

Qcool, total … total annual cooling demand of all buildings in kWh/a

pHC,energy … cooling energy price in €/kWh

Roverall=Rheat+Rcool+pconnect⋅Ntotal⋅a

Roverall … overall revenues of the system in €/a

Rheat … annual heating revenue in €/a

Rcool … annual cooling revenue in €/a

pconnect … connection fee per building in €/building

Ntotal … total number of buildings

a … annuity factor

## Investment Costs

Cnet=cnet⋅ltotal

Cnet … total investment cost for the network in €

cnet … specific investment costs for the network in €/m

ltotal … total net length in m

Ci=ci⋅Qheat, supply

Ci … total investment costs per heat supply in €

ci … specific investment costs per heat supply in €/(kWh/a)

Qheat,supply … annual heating supply per source in kWh/a

Ci,total=j=1nCi

Ci,total … total investment for total heat supply in €

Ci … total investment costs per heat supply in €

n … number of sources

Coverall=CHP⋅Ntotal+Cnet+Ci+Ci,total

Coverall … overall investment costs of the system in €

CHP … investment costs of a heat pump in €

Cnet … total investment cost for the network in €

Ci … total investment costs per heat supply in €

Ci,total … total investment for total heat supply in €

a=1+ip⋅i1+ip-1

a … annuity factor

p … depriciation period in years

i … interest rate

Cannual=Coverall⋅a

Cannual … annualized costs in €/a

Coverall … overall investment costs of the system in €

a … annuity factor

## Operational Costs

Cel=i=1nQheat, supplyCOPH⋅cel+i=1nQcool, supplyCOPC⋅cel

Cel … total costs for electricity of heat pumps in kWh/a

Qheat,supply … annual heating supply per source in kWh/a

Qcool,supply … annual cooling supply per source in kWh/a

COP … Coefficient of power of heat pump per source

cel … specific electricity costs in €/kWh

Consider a cost reduction, when PV is available.

## Additional Costs

CO&M=0.02⋅Coverall

CO&M … annual operation & maintenance costs in €/a

Coverall … overall investment costs of the system in €

# Evaluation and Interpretation of the Results

The tool evaluates the calculated indicators using the predefined thresholds below. Each indicator should be presented with its classification and a short explanation of what it means for the project.

## Heating and Cooling Supply Coverage

Heating and cooling coverage should be assessed separately. The applicable coverage classification should be shown for each, with the implications for the overall result explained.

Table 6: Classification of Heating and Cooling Supply Coverage

| Coverage | Classification | Interpretation |
| --- | --- | --- |
| Above or equal 100% | Feasible | Sufficient annual energy potential to cover the total demand with additional potential available. |
| 90-99.9% | Conditionally feasible | A small share of supplementary supply is required. |
| 70-89.9% | Limited feasibility | A significant share of supplementary supply is required. |
| Below 70% | Not feasible as the sole supply concept | Too much demand remains uncovered. |

## Building Density

Table 7: Classification of Building Density

| Building Density | Classification | Interpretation |
| --- | --- | --- |
| Above 30 buildings/ha | High density | Densely built areas can benefit from shorter network lengths, although low energy demand may still weaken economic performance. |
| 10-30 buildings/ha | Medium density | The structure may be suitable for a network. |
| Below 10 buildings/ha | Low density | Buildings are more distributed, potentially increasing network length. High energy demand or suitable local energy sources may still make a project promising. |

## Heat Density

Table 8: Classification of Heat Density

| Heat Density | Classification | Interpretation |
| --- | --- | --- |
| Above 1.5 | High density | A relatively short network serves a high heating demand, potentially improving economic performance. |
| 0.5-1.5 | Medium density | The network may be viable. |
| Below 0.5 | Low density | A relatively long network serves a low heating demand. Substantial cooling demand or low network costs may improve the outlook. |

## Cooling-to-Heating Ratio

The cooling-to-heating ratio is an indicator of the potential for thermal balancing. It does not automatically determine whether a network is feasible, but it can influence the required system configuration and economic viability.

Table 9: Classification of C/H-Ratio

| C/H Ratio | Classification | Interpretation |
| --- | --- | --- |
| 0.8-1.0 | Balanced | Heating and cooling demand are similar, potentially supporting thermal exchange. |
| 0.3-0.8 | Partially balanced | One demand is higher than the other, but thermal exchange may still be possible. |
| Below 0.3 | Unbalanced | One demand clearly dominates, potentially increasing the need for external energy sources or thermal storage. |

## Overall Assessment Rule

The overall assessment combines technical supply coverage, spatial suitability and economic viability. The purpose is to provide a transparent initial screening result rather than a definitive feasibility decision. The tool shall provide one of three overall results.

Table 10: Overall Result Classification

| Result | Classification |
| --- | --- |
| PROMISING | All relevant heating and cooling demands have at least 90% annual supply coverage, the economic assessment is favorable and building density and heat density are both not classified as low. |
| FURTHER ANALYSIS REQUIRED | Essential information is missing or uncertain, coverage is between 70%-90%, heat and building density indicators are mixed or the technical and economic results do not support a clear conclusion. If the project area includes industry. |
| NOT PROMISING | The economic assessment is clearly unfavorable, or relevant supply coverage is below 70% and both building density and heat density are low. |

The tool should display the overall result together with the main factors supporting or limiting it. This ensures that users understand the reasoning behind the assessment and can identify which aspects require further investigation. The overall assessment is a preliminary screening result and does not replace a detailed technical or economic feasibility study.